Backup Diesel Generator Mockup Screen

1. Screen Purpose (Reduced)

Answer only:

- can it start

- can it be controlled

- is it running

- what is blocking it

- what state is it in

2. Layout (Same Structure, Reduced Content)

Keep same layout as reference:

- Top tab bar (max 4 tabs)

- Left asset panel (one-line + commands)

- Right panel (status + logic)

- No extra visuals

3. Tabs (Reduced to 4)

- Overview

- Control / Modes

- Start Readiness

- Alarms

4. Top Header (Minimal)

Left

- Backup Diesel – EDG

- State badge

Right (commands)

- Start

- Stop

- Auto

- Alarm Ack

5. Left Panel (Minimal)

One-line

- Generator → Breaker → Bus (symbolic only)

Controls

- Start

- Stop

- Auto

No additional info here.

6. Overview Tab

Cards (only what is derivable from mapping)

- Operating State

  - INIT / STARTING / RUNNING / etc

  - (0x009A Auto Start Stop State)

- Control Mode

  - STOP / AUTO / RUN

  - (0x0000, 0x00A2)

- Control Authority

  - Allowed / Not Allowed

  - Derived:

    - Engine Mode == AUTO

    - Generator Not in Auto == FALSE

- Ready to Start

  - Yes / No

  - Derived:

    - Starter Mode = “Start Not Requested”

    - No shutdown active

    - In AUTO

- Shutdown Active

  - Yes / No

  - (0x00281)

- Running

  - Yes / No

  - Derived from:

    - Operating Mode == RUN
OR

    - Auto Start Stop State == RUNNING

7. Control / Modes Tab

Focus: command permissives

Cards

- Engine Operating Mode (0x0000)

- Control Switch Position (0x00A2)

- Generator Not in Auto (0x00263)

- Shutdown Active (0x00281)

Derived status

- Master Control Allowed

  - TRUE when:

    - Mode == AUTO
AND

    - Not in Auto == FALSE

- Command Status

  - Last command state (STOP/AUTO/RUN)

8. Start Readiness Tab

Focus: “why won’t it start”

Primary driver

- Starter Mode (0x021A)

  - Use directly as explanation

Supporting states

- Shutdown Active

- Hard Shutdown (0x0003)

- Soft Shutdown (0x0004)

- Emergency Shutdown (0x0215)

Derived

- Ready to Start = TRUE only if

  - Starter Mode = Start Not Requested

  - Mode = AUTO

  - No shutdown conditions

9. Alarms Tab

Only include mapped blockers.

Grouped

Shutdown / Trip

- Shutdown Active (0x00281)

- Hard Shutdown (0x0003)

- Soft Shutdown (0x0004)

- Emergency Shutdown (0x0215)

Control Blocking

- Generator Not in Auto (0x00263)

- Engine Auxiliary Switch / E-Stop (0x00262)

Start Fail / Protection

- Overcrank (0x00264)

- Overspeed (0x00265)

Thermal / Mechanical

- High Coolant Temp (0x00269)

- Low Oil Pressure (0x00271)

- Low Coolant Level (0x00273)

Other

- Air Damper Shutdown (0x0026C)

- High Battery Voltage (0x0026E)

- Low Fuel Level (0x00275)

- SCR Fault (0x00278)

10. Commands (Strict Mapping)

- Start

  - Write 2 → 0x006C

- Stop

  - Write 0 → 0x006C

- Auto

  - Write 1 → 0x006C

No other commands exposed.

11. UX Rules (Reduced)

- No electrical data

- No temperatures/pressures

- No blackout recovery logic

- No inferred plant-level context

Visual priorities

- Can I control it

- Can it start

- Why not

12. Minimum Mockup (Final)

Header

- Name

- State

- Commands

Left

- One-line

- Start / Stop / Auto

Right (Overview)

- Operating State

- Mode

- Control Allowed

- Ready to Start

- Shutdown Active

Tabs

- Overview

- Control / Modes

- Start Readiness

- Alarms